34

10130010044

MACON

INSTALLATION & INSTRUCTION
MANUAL

AIR TO WAT ER
HEAT PUMP
(EVI MODE)

Macon Cooling and Heating Energy-efficient Equipment Co., Ltd
N o t i c e

1.1 In order to use this product better and safer, please read this instruction care full y befor e insta ll and operate it. Please pay attention to all the notice in operation and maintenance. Save all manuals and doc umen tati on for f utur e reference.

1.2 Air to water pump is a special appliance. Improper installation will cause damage and danger. It should be installed and maintained by the professionals. Please conta ct our authorized loca l service point for installation and maintenance. Please read and follow this instruction carefully before and during ins tallati on. Remarks:
We will not bear the responsibility for any personal injury or unit damage caused by non-Compliance of the regulations and instruction in this manual.

1.3 Please check whether the distribution power capacity, switch and socket
are compliance with the requirements of our unit power. Details please refer to the rating label or parameter table in this manual.

1.4 The power should be equipped with leakage protection separately.
Power cable should be chosen in accordance with the operation requirements of the unit.

1.5 The unit must be grounded safely. Do not use the unit if grounded unsafely.
Do not connect the ground line to the neutral and or tap water pipe.

1.6 The wire must be joined in compliance with the requirements of the wiring chart.
Do not alternate and or repair the unit personally.

1.7 Do not install the unit closed to inflammable, explosive and naked light spot.

1.8 To ensure the unit operate properly, please equipped with a filter in the water input when installation.
CONTENTS
I. Specification................................................................. 1
1. Model Nomenclature(indoor unit)........................................... 1
2. Model Nomenclature(outdoor unit)......................................... 1
3.Parameter of multi-function air to water heat pump................... 1
4. Installation dimensions of indoor unit................................... 2
5.Installation dimensions of outdoor unit...................................... 2
II. Installation................................................................... 3
1. Unit installation position........................................................ 3
2. Installation requirement......................................................... 4
3.Water tank installation select................................................... 4
4.The unit and water tank installation .......................................... 4
5.The refrigerant piping connection for split type unit .................... 5
6.Water pipe connection............................................................. 7
7.Trial operation........................................................................ 8
8. Installation of terminal equipment............................................ 8
9.Installation of the temp detector ............................................... 9
10.Electrical wiring ..................................................................... 9
III. Use.............................................................................. 11
1. Function diagram of the remote controller................................ 11
2. Operation and display............................................................ 11
3. System state parameter checking........................................... 14
4. System parameter setting...................................................... 15
5. The maintenance time inquires............................................... 17
6. Date/time/timing on and off settings........................................ 17
7. Lock button/Ddfrost status/Fahrenheit and celsius change....... 18
8. Fault code display................................................................. 18
9. Parameter table.................................................................... 19
IV. Installation sketch....................................................... 20
1. Hot water mode installation drawing....................................... 20
2. Heating mode installation drawing ......................................... 21
3. Hot water&Heating or cooling mode installation drawing .......... 22
V. Maintenance and repair................................................ 23
1. Malfunction Indicating Table.................................................. 23
VI. Wiring diagram ........................................................... 24
1. Mk3092 PCB input and output port definition ........................... 24
2.The electrical box of internal structure .................................... 25
3.MK3077 Power protection board setting.................................. 27
4.Unit wiring diagram ............................................................... 28
I. Specification
1. Model Nomenclature(indoor unit)
MA CHR W S W A /P S(B 01 D)
Source medium
MD: Dual source
(air source +ground source) MA: Air source
MW: Ground source Function of the unit C: Air co oling
R: Air he ating
CH: Air cooling and hot water CR: Air cooling and heating HR: Hot water
CHR: Air (heating+cooling) and hot water
Energy exchange medium
A: Refrigerant W: Water S:with solar
(Without solar omitted)

The figure represents the horse power of unit eg:010 means 1 horse power

2. Model Nomenclature(outdoor unit)
MA FP A ( )

D:With electrical heating
(Without electrical heating omitted)
Design serial number

B: Inverter
E: EVI
(Without inverter or EVI omitted) S:3phase (single phase omitted)
P:With built in pump
(Without built in pump omitted)

A: Horizontal fan direction B: Upward fan direction C:Double air duct type
(Omit the split type unit model)

Z: Integrated type
W: Split type(indoor unit )

Energy exchange medium
MA: Refrigerant
MW: Water
FP: Fan coil

3.Parameter of double source heat pump

Design alternative serial number
A: Horizontal fan direction
B: Upward fan direction
The figure represents the horse power of unit eg:010 means 1 horse power

Indoor unit model	MACHRW(S)	050W/(E01)	050W/S(E01)	080W/S(E01)	100W/S(E01)
Outdoor unit(Side fan) mode	MAFP	050A	050A	080A	100A
Rated Cooling Capacity	kW	13.0	13.0	20.8	26.0
	BTU/h	44400	44400	71000	88800
Rated Input Power(Cooling)	kW	4.33	4.33	6.93	8.67
Rated Input Current(Cooling)	A	19.7	6.6	10.6	13.2
Rated Heating Capacity	kW	15.0	15.0	24.0	30.0
	BTU/h	51200	51200	81900	102400
Rated Input Power(Heating)	kW	4.80	4.80	7.70	9.60
Rated Input Current(Heating)	A	21.9	7.5	12.0	15.0
Electrical heating	kW	4.0	4.0	4.0	4.0
Rated Input Current	A	19.0	19.0	19.0	19.0
Rated Output Water	L/h	380	380	600	750
Power Supply	V/PH/Hz	220/1/50	380/3/50	380/3/50	380/3/50
Compressor		Scroll	Scroll	Scroll	Scroll
Compressor Qty		1	1	1	1
Fan Qty		2	2	2	2
Noise	dB(A)	58	58	60	60
Refrigerant Liquid Pipe	inch	1/2	1/2	5/8	5/8
Refrigerant Gas Pipe	inch	5/8	5/8	7/8	7/8
Refrigerant Gas Type		R410A/R407C
Water Connection	inch	1	1	1-1/4	1-1/4
Water Flow Volume	m3/ h	4.0	4.0	6.0	7.0
Indoor Unit Net Dimensions(L/W/H)	mm	670/600/760	670/600/760	1230/730/800	1230/730/800
Indoor Unit Shipping Dimensions(L/W/H)	mm	730/650/810	710/670/780	1280/760/840	1280/760/840
Outdoor Unit Net Dimensions(L/W/H)	mm	730/650/810	930/440/1270	1105/470/1540	1105/470/1540
Outdoor Unit Shipping Dimensions(L/W/H)	mm	1080/480/1310	1050/450/1310	1145/500/1580	1145/500/1580
Indoor Unit (Net/Shipping)Weight	kg	145/160	145/160	200/230	200/230
Outdoor Unit (Net/Shipping)Weight	kg	60/65	60/65	65/75	65/75

Note: (1)The manual is a technical parameters measured in the following conditions: outdoor dry temperature is 7 and wet bulb temperature is 6 ,the temperature of water inflow is 15 and of water outflow is 55 .
(2)Using in ambient temperature:-25 45
4.Installation dimensions of indoor unit

Units: mm

MODEL / Size	MACHRW050(E01) MACHRW050/S(E01)
A	450
B	640

B

G
Units: mm
Size MACHRW	100W/S(E01)	Meaning
A	800	High
B	1230	Length
C	730	Wide
D	750
E	710
F	4- 12	Mounting hole
G	1-1/4	Hot water outlet
H	1-1/4	Hot water inlet

A H

C

E

D F

5.Installation dimensions of outdoor unit

Units: mm
MODEL / Size	MAFP060A MAFP040A
A	525
B	440

A B

Units: mm
Size MAFP	080A 100A	Meaning
A	1540	High
B	1105	Length
C	470	Wide
D	725
E	485
F	4- 12	Mounting hole

A

       D F

E C

B

II. Installation

1. Unit installation position
To avoid ventilation short, the r unit discharged air should not return when installation. Please keep enough space around the unit for repair. Right and wrong means as below:
MACON

Wrong	Right

Notice:

1. To get enough air for ventilation of the unit, the installation position should be with good ventilation.
2. The installation position can hold the outdoor unit without noise and shake.
3. No sunlight to the unit. Set an awning if necessary.
4. The water from rain and defrosting can be discharged in the installation position.
5. The unit will not be covered by snow in the installation position.
6. The discharged air will not face strong air in the installation position.
7. Assure the noise caused by the unit ventilation and operation will not affect the neighbour.
8. The installation position will not be affected by garbage, oil and mist.
9. The unit will be damaged under the condition with oil(engine oil), salt(sea area)
and sulfide air(near thermal spring and refining factory).
2. Installation requirement
2.1 The unit can be installed in the balcony, roof, floor or any other convenient place and reliable load-bearing.
2.2 Airiness place.
2.3 No heat radiation or other heat source place
2.4 Should be set up shed against the snow in winter.
2.5 Barrier-free at the air inlet or outlet place.
2.6 Outlet against strong winds blowing place.
2.7 There should be drainage channels around the machine in order to rule out the condensate.
2.8 Control Panel, do not install in the bathroom, so as not to affect the unit work by wet.
2.9 Should leave enough space around the machine. As shown below.
A. Side fan type installation space requirements:
500mm

600mm
Air intlet
300mm
Unit

1500mm
Air outlet
200mm

600mm
200mm

500mm

Unit

600mm

Unit

Bolt
 fix
Bolt
 fix

200mm

B. Top fan type installation space requirements:

2000mm

600mm

700mm
400mm
700mm

400mm

400mm

Bolt fix

1000mm

1000mm

3.hot water tank and buffer tank install location select
3.1 The water tank can be installed in the outdoor with heat pump outdoor unit, such as balconies, roofs, floors, also can be installed in the room.
3.2 Water tank must be standing install, the installation place is a solid foundation, must be bear the weight of the tank when full of water.
3.3 Around the water tank , as well as water pipes and hot water pipes should install a valve.
3.4 Do not install the water tank, where exist pollute and corrosive gases.

4.The unit and water tank installation
4.1 Unit install base is concrete structures, also can be made of steel angle brackets, plus vibration rubber pad placed on the ground or roof, to ensure the unit horizontally.
4.2 Installed base design should in accordance with units and water tanks installed size
And operational quality.
4.3 Directly use expansion bolts to fix unit and water tank to the concrete base.
4.4 Around the unit and tank should be drain or outlet.
5. The refrigerant piping connection for split type unit

5.1 Each component's names and function of refrigerant stop valve

Adapter connector

The connecting pipe joint of indoor unit and

Indoor unit and outdoor unit copper connecting pipe

outdoor unit . Needle valve

To discharge the air in the connecting pipe
and outdoor unit by refrigerant pressure or connect a vacuum pump.
Valve plug

Turn on or turn off the stop valves.

Adapter connector

Needle valve

Needle valve nut

Stop Valves

Adapter connector nut

valve plug

valve plug nut

5.2 The unit refrigerant pipe connecting

A: According to the indoor and outdoor unit fixed location and location of holes through the wall, choose a good direction lead to pipe. Then begin the indoor pipe connection work.
B: Use a wrench to remove the adapter
connector nut;
C: As shown on the right, press the trumpet on the connector cone, then hold the connection pipe

Connecting pipe

Copper pipe

Flare nut

Adapter connector

Copper pipe

with one hand, so that keep the connector axis in the first line, the other hand the gradually screw the flare nut on the connector, then tighten with wrench.

5.3 Air discharge ( by indoor unit refrigerant)

Low pressure valve
High pressure valve
If the system is small, use refrigerant empty way to discharge the pipe and outdoor unit air,
to discharge the air in the connecting pipe and outdoor unit, when there's refrigerant in the pipes originally, just open the low pressure side needle valve of indoor unit to discharge the air by refrigerant pressure. As the following steps:
A: Unscrew the valve plug nut on the stop valve , and unscrew the needle nut on the indoor unit low pressure side.
B: Open the stop valve at outdoor unit high/low pressure side by valve plug.

C: Open the stop valve at indoor unit's high pressure side by valve plug, Note: don't open the one at low pressure side.
D: Open the needle valve by small screwdriver , and this outlet will discharge the air in connecting pipe and outdoor unit at the same time.
E: Close the needle valve after open it about 10-20 seconds ,The time is according to the size of outdoor unit and the length of the connecting pipe.
F: After the air discharging, open the stop valve at the indoor unit low pressure side
G: Screw and close the screw cap on the stop valve
As the picture show

Big pipe

1

Small pipe

Low pressure side

High pressure side

Low pressure side

High pressure side

valve plug
valve plug
valve plug
valve plug

Needle valve
Needle valve
Needle valve
Needle valve

2
valve plug nut

valve plug nut
Indoor unit Outdoor unit

NOTE 1 : The direction of the arrow is the air discharging flow direction which is same as the refrigerant flow direction. NOTE 2 : The air is discharged from this outlet

5.4 Air discharge ( by vacuum pump)
If the system large or after maintenance of outdoor system, should use the vacuum pump discharge way to empty the air and water within the system.

As the following steps:
A: As the picture show, connect the vacuum pump with the pressure gauge, and then connect the vacuumed connecting pipe with the needle valve on the indoor unit low pressure side.

Outdoor unit
B:	Unscrew the valve plug nut on the stop valve , and unscrew the needle nut on the indoor unit low pressure side.
C:	Open the stop valve at outdoor unit high/low pressure side by valve plug.
Note: Do not open the indoor unit high/low
pressure side stop valve.

High pressu

Stop valve

Low pressure side
re sid	e

Stop valve

      Hose

D: Open the compound pressure gauge and vacuum pump to vacuum the outdoor unit and pipe, so that the absolute pressure not higher than 130Pa, and keep the pressure does not rise within 5 minutes after vacuum.
E: After the air discharging(vacuumming),disconnect the connecting between the pressure gauge and indoor unit stop valve .
F: Open the stop valve at indoor unit high/low pressure
side by valve plug, then let the indoor unit's refrigerant

Indoor unit

Composite table

Vacuum pump
flow in outdoor unit(if need to add more refrigerant, please refer to 2.4).
5.5 Add refrigerant
When the pipe is too long, please add
ad dit ion al refrigerant as following formula: Additional refrigerant amo un t=
(one-way tube length -5) x (0.015~0.02) kg, choose 0.015 or 0.02 according to the size
of diameter.

High pressure

Outdoor unit

Low pressure side

R ef rig er an t

choose 0.015;
when the diameter = 15.88, choose 0.02 . The methods to add refrigerant
refer to the right diagram :

5.6 Leak check
Stop valve

Indoor unit

Composite table

Scale
After discharge the air, use electronic leak detector or soapy water to test all the connectors in the indoor and outdoor unit.
6. Water pipe connections

6.1 Pipe should be a kind of pipe that heat-resistant,rust-proof, uneasy-fouling.and in co nfor mity w ith national health and safety standards, which can be stainless steel pipe, co pper pi pe, al umi num water pipe, hot water PPR pipes and so on.
6.2 Water tank outlet pipe and overflow pipe is better to installed around the gutter or sewer, so that to convenient to drainage.
6.3 The connection of the heat pump unit and water tank must be installed a stop valve or dismountable loose joint, for maintenance use.
6.4 Water pipes are arranged reasonably to minimize bending and reduce the pressure loss of water system .
6.5 The connection of tap water pipe and water filling connection must install one-way valve, f ilter, supply water solenoid valve (for tank-type water tank) and pressure relief devices
(for close-type valve the parameter value is 0.7MPa), installed when valve body arrow is same as with the flow direction to prevent water block. The cycle water outlet of the heat pump unit should connect to the inlet of water tank , The cycle water inlet of the heat pump unit should connect to the outlet of water tank, the water supply inlet of the tank should connect to the heat water supply outlet . The entire piping system should be clean,
no rust and dirt residue to prevent pipe blockage.
6.6 After the installation of the water filling pipe and cycle water pipe and hot water supply pi pe , all the pipes should take the water tightness test. And ensure that the system is clean. And then cover insulation on the pipe and valve (including the supply water pipes and valves).
6.7 Power line and signal line layout should be neat, rational, strong and weak lines separating cable and Can not interfere with each other, without contact with the connecting pipe and valve.
6.8 After the construction of all wiring is completed, carefully check the correct order to connect the power.
6.9 Unit electric wire connection: connect to the appropriate terminals according to wiring diagram, and fix it by the pressure line of board in the electrical box.
6.10 All the wiring construction is completed, can be plugged in only after careful examination correctly.
6.11 Unit control board fuse parameters: 5A/220V.
6.12 The unit wire controller must be fixed in the bottom of standard electrical switch box.
7. Trial operation(should be operated by professionals)

7.1 Check before trial operation

A: Check the pipe system. Check the whole pipe system. Ensure the water volume in the system is full and the air is exhaus ted complet ely. Check whether the valve is open throughout the system and the thermal insulating of the pipe is well.
B: Check the power supply and distribution system. Check whether the power supply voltage is normal, the power distribution accessory screws all tighten, supply power is in compliance with the wiring diagram and the wire is grounded well.
C: Check the air cooled water chiller. Check whether any screw loose. Check the signal indicator light (green) of the outdoor unit control panel is illuminated normally and the fault indicating lamp(red) is illuminated. Connect the pressure gauge to the freon feed mouth for checking the pressure during operation. Disconnect them after test is ok.
7.2 Trial operation
A: Press on/off in the remote controller turn on the hot water circulating pump whether t he water pump operates normally. Observe and determine whether air pipe is exhausted completely, flow switch is closed, hydraulic pressure indicated in the pressure gauge is more than 0.2MPa.Come to next step after confirm the circulating water system works normally.
B: Press on/off in the remote controller, the water pump and fan start immediately.
The compressor start after the unit operates for some time. Observe and determine if there's any abnormal sound during operation. Stop to check the unit if there's abnormal sound. The unit can continue to run only when there's no abnormal sound. Check whether the cooling system pressure is normal at the same time.
C: Check whether the input power and current of the unit are compliance with the parameter in this Instruction. If not, stop to check the unit.
D: Observe whether the outlet water temperature is normal.
E: Parameter of the remote controller has been set before leave of the factory. Never alternate them personally.
8. Installation of terminal equipment
8.1 Indoor terminal equipment installation (such as: fan coil, radiator heater or floor heating), the equipment should be installed in accordance with relevant regulatory requirements.
8.2 In accordance with the requirements of engineering design drawings, installation and construction.
8.3 Use a soft connector to connect the unit and fan coil inlet and outlet pipes; install fan coil condensate drain pipe, connect the condensate drain interface, and to ensure smooth drainage of condensate water.
9 . I n s t a l l a t i o n o f t h e t e m p d e t e c t o r

D e t e c t o r
Ta n k

D e t e c t o r
Ta n k Ta n k Ta n k
D e t e c t o r D e t e c t o r
T h e h e a d

T h e h e a d o f s e n s o r

c o n d u c t i o n s i l i c a g e l

T h e h e a d o f s e n s o r

< 5 p i n

T h e h e a t
c o n d u c t i o n
s i l i c a g e l

o f s e n s o r

< 5 p i n

< 5 p i n

T h e h e a t
c o n d u c t i o n
s i l i c a g e l

The first step The second step The third step The fourth step

9.1.The first step Daub the heat conduction silica gel spreads in the front of sensor, and insert into the detector.
9.2.The second step use < 5 pin to push the detector into the end of the detector against the end of the sensor, and marks on level of the pin and the detector.
9.3 The third step putout the pin the position of mark to be at the same level with the inlet of detector	check whether the sensor is inserted to the pipe terminal.
9.4 The fourth step the inlet of the detector is sealed with the glass silica gel, and keep the inlet
of the detector upwards and uprightness about an hour.

10. Electrical wiring
10.1 The unit should use dedicated power supply, power supply voltage line corresponding with rated voltage.
10.2 The unit power cable must use copper cable, the cable diameter must ensure that the unit's maximum starting current requirements.
10.3 The unit power supply circuit must have a grounding wire, which should connect with a reliable external ground wire, and the external ground wire is effective.
10.4 Wiring construction must be installed by professional technicians refer to circuit diagram.
10.5 Power lines and signal line layout should be neat, rational, strong and weak lines separate and can not interfere with each other, while not contacted with the connecting pipe and the valve body.
10.6 When power lines and control lines parallel, the wires were placed in each tube, also leave appropriate distance between the lines.
10.7 Unit electric wire connection: take the unit power line, remote control three core lines, electric heater power line, solar circulated water pump control power line, water tank temperature sensing line, solar collector temperature sensor line, terminal equipments connect to unit lines, through the unit wiring hole set into the electrical box, connect to the appropriate terminals according to wiring diagram, and fix it by the pressure line of board in the electrical box.
10.8 Unit control panel Code Mk3092, Fuse specifications: 5A/250V
10.9 Power wiring as follows (single unit):

A:Heat pump unit power input

L N R S T N

Ground line
Zero line
Phase line 3
Phase line 2
Phase line 1
Ground line
Zero line
Phase line

Mode	Host Power	Phase line	Zero line	Ground line	Max.line length (m)	Signal line	Tem. sensor assistance line	Max.line length (m)
050W(E01)	220V/1PH/50Hz	6.0mm2	6.0mm2	6.0mm2	15	0.5mm2	0.5mm2	50
050W/S(E01)	380V/3PH/50Hz	4.0mm2	4.0mm2	4.0mm2	15	0.5mm2	0.5mm2	50
080W/S(E01)	380V/3PH/50Hz	6.0mm2	6.0mm2	6.0mm2	15	0.5mm2	0.5mm2	50
100W/S(E01)	380V/3PH/50Hz	6.0mm2	6.0mm2	6.0mm2	15	0.5mm2	0.5mm2	50

B:Auxiliary electric heater power input

Mode	Host Power	Phase line	Zero line	Ground line	Max.line length (m)	Signal line	Tem. sensor assistance line	Max.line length (m)
0.40Kw	220V/1PH/50Hz	4.0mm2	4.0mm2	4.0mm2	15	0.5mm2	0.5mm2	50
0.75Kw	220V/1PH/50Hz	8.0mm2	8.0mm2	8.0mm2	15	0.5mm2	0.5mm2	50

Note:
1. used PVC insulated copper wire for above wiring
2. for installation requires, the line is longer than the maximum line length, please contact the company
III. USE

1. Remote controller interface displays as below

Prg

Ese
Welcome to use

2. Operation and display
	UNIT / ON/OFF	Press this button to control the unit's / ON or OFF
Prg	SET	Press this button to enter the main menu interface
Ese	BACK	Press this button to return to the previous / screen
	UP	Modify theparameter values or turn to next page
	DOWN	Modification parameter values or turn to next page
	ENTER	Press this button and enter the next parameters interface or enter parameters modification state, and confirm the modification

2.1 . Power on(off)/mode display status

MODE
Off
MODE
Hot water

	A.C. water Inlet	12		A.C. water Inlet	12
Prg	Hot water tank	25	Prg	Hot water tank	25
	Solar Collector	25		Solar Collector	25
Ambient temp. 30 Ambient temp. 30 / Ese 2013-04-08 11:25 Ese 2013-04-08 11:25

Power off
Power on

2.2 Mode of operation
Under the main interface,press:

Prg

enter into parameter setting interface,choose
"main menu ",press button,choose "Mode select",press into the mode setting, press to view and choose,press again to go into the modify parameter interface, the corresponding parameter value is flashing,press to modify the value,press
Ese
(E.g)
eturn to the previous menu.

Prg

Ese
MODE

Hot water tank
Solar Collector

2013-04-08 11:25
Off

25
25

Prg

Ese
Main menu
Maintenance

Water supply setting Prg

Ese
Mode select
Unit status

Press
Prg
button
Press
button

Press button you can change the running mode
    Press button you can change the set heating temp.
Mode		Heating / Hot water		Press	button you can		Mode	Heating / Hot water
A.C.heat temp. 38 A.C.heat temp. 38

	Aux.heating		on	Press	button you can turn on/off		Aux.heating		on
Ese Priority A.C/H.W auxiliary electric heater Ese Priority A.C/H.W

Press button again

Prg

Hot water temp. 55
change the set hot water temp.

Prg

Hot water temp. 55

     Press button you can choose the priority of air condition or hot water.
2.3 Mode introduction

There are six selection modes, the following is the mode of display and introduction

Cooling mode

Mode	Cooling	1.1 Hot water temp.	55	4.1 Power memory	On
		1.2 H.W T	5	4.2 Economic mode	Off
A.C. cool temp.	12	1.3 Heating temp.	40	4.3 H.W.pump	Normal

Prg Prg		1.4 Heating T / 1.5 Cooling temp.	5 / 12	Prg	4.4 EVI valve 5 / 4.5 Comp.PT temp. 105
Ese	Ese	1.6 Cooling T	5	Ese	4.6 E.H.H.W.pump Special / 4.7 Cooling mode Off / 4.8 Elec.mode Heat&H.W

The parameter setting of cooling mode
1.Parameter 1.5 under air condition side cooling mode,the setting of water inlet temperature .
2.Parameter1.6 under air condition side cooling mode,the compressor restart difference temperature.
3.Parameter4.7 whether open the cooling function to the user interface
On:open Off: don t open

Heatling mode

Prg

Ese
Aux. Heating
Off
Prg

Ese
1.4 Heating T 5
1.5 Cooling temp. 12

Mode	Heating		1.1 Hot water temp.	55		3.1 Aux.elec. T	5
			1.2 H.W T	5		3.2 Aux.start delay	30M
A.C.heat temp.	40		1.3 Heating temp.	40		3.3 Ambient temp.set	15

1.6 Cooling T 5
Prg

Ese

The parameter setting of Heatling mode
1.Parameter 1.3 under air condition side heating mode,the setting of water inlet temperature .
2.Parameter 1.4 under air condition side heating mode,the compressor restart difference temperature.
3.Note: when Aux.heatinig is ON, and the electric heater also meet the requirement of parameter3.1~3.3, so then the electric heater can work.
Parameter 3.1 :Under hot water electric heating mode, the electric heating restart difference temperature.
Parameter 3.2: Auxiliary electric heater start delay time (the time to delay after unit power on, the electric heater allows to output).
Parameter 3.3:The auxiliary electric heater start ambient temperature(When the ambient
temperature is below the set temperature, the electric heating allows the output .

Hot water mode

4.7 Cooling mode

Prg	Mode	Hot water			1.1 Hot water temp.	55			4.1 Power memory On
					1.2 H.W T	5			4.2 Economic mode Off
	Hot water temp. / Aux. Heating	55 / on		Prg	1.3 Heating temp. / 1.4 Heating T	40 / 5		Prg	4.3 H.W.pump Normal / 4.4 EVI valve 5
					1.5 Cooling temp.	12			4.5 Comp.PT temp. 105
					1.6 Cooling T	5			4.6 E.H.H.W.pump Special
Ese				Ese				Ese	4.8 Elec.mode Heat&H.W

Off
The parameter setting of hot water mode
1.Parameter 1.1 the setting temperature of hot water.
2.Parameter1.2 hot water mode,the compressor restart difference temperature.
3.Parameter4.3 hot water cycle pump working mode option.
Special:hot water tank temp. reaches the set temperature, the hot water cycle pump keep working.
Normal:hot water tank temp. reaches the set temperature, the hot water cycle pump stop working.
4.Note: when Aux.heatinig is ON, and the electric heater also meet the requirement of parameter3.1~3.3, so then the electric heater can work.
Parameter 3.1 :Under hot water electric heating mode, the electric heating restart difference temperature.
Parameter 3.2: Auxiliary electric heater start delay time (the time to delay after unit power on, the electric heater allows to output).
Parameter 3.3:The auxiliary electric heater start ambient temperature(When the ambient
temperature is below the set temperature, the electric heating allows the output .

Heating+Hot water mode

Ese
Mode Heating
Hot water
A.C.heat temp. 40
Prg	Hot water temp.	55	Prg

Priority H.W
				4.7 Cooling mode Off
Ese					Ese	4.8 Elec.mode Heat&H.W

1.1 Hot water temp. 55
1.2 H.W T 5
1.3 Heating temp. 40
1.4 Heating T 5

1.5 Cooling temp. 12

Prg
4.1 Power memory
4.2 Economic mode
4.3 H.W.pump
4.4 EVI valve
4.5 Comp.PT temp.
On Off Normal
5
105

Cooling+Hot water mode

Hot water temp. 55
Prg
1.4 Heating T 5
Prg
4.4 EVI valve 5

4.7 Cooling mode

Prg	Mode	Cooling			1.1 Hot water temp.	55			4.1 Power memory	On
		Hot water			1.2 H.W T	5			4.2 Economic mode	Off
	A.C.cool temp.	12			1.3 Heating temp.	40			4.3 H.W.pump	Normal

	Priority	H.W			1.5 Cooling temp.	12			4.5 Comp.PT temp. 105
					1.6 Cooling T	5			4.6 E.H.H.W.pump Special
Ese				Ese				Ese	4.8 Elec.mode Heat&H.W

Off

Note:Parameter4.7 whether open the cooling function to the user interface
On:open Off: don t open

Manual operation electric heater mode

Legend:
MODE Off MODE Off					This icon means the manual
	A.C. water Inlet	12		A.C. water Inlet	12		electric heating model is in
Prg	Hot water tank	25	Prg	Hot water tank	25		operation
	Solar Collector	25		Solar Collector	25
Ambient temp. 30 Ambient temp. 30 / Ese 2011-04-08 11:25 Ese 2011-04-08 11:25

Press button for 5 s
(turn on the mode)
The parameter setting of Manual operation electric heater mode

1.Parameter4.6 when the unit running manual electric heating mode the hot water cycle pump working way.
Special:the hot water cycle pump required output. Normal:the hot water cycle pump not required output.
2.Parameter4.8 the application of manual electric heater
Heat: air condition heating auxiliary electric heater
Heat&H.W: air condition heating and hot water auxiliary electric heater

Manual operation water supply function

Legend:
MODE Off MODE Off					This icon means the manual
	A.C. water Inlet	12		A.C. water Inlet	12		water supply output is in
Prg	Hot water tank	25	Prg	Hot water tank	25		operation
	Solar Collector	25		Solar Collector	25
Ambient temp. 30 Ambient temp. 30 / Ese 2011-04-08 11:25 Ese 2011-04-08 11:25

Press button for 10 s
(turn on/turn off the water supply )

Automatic water supply function

Parameter 7.1 whether turn on the automatic constant temp. water supply function,
7.1 Water supply On
7.2 Supply temp. 40
7.3 Supply T 5
ON means turn on (work with parameter 7.4,) OFF means turn off
Parameter 7.2 the water supply return temp. setting
Prg

Ese
7.4 Timer 16:00-23:00
Parameter 7.3 the temp. difference between the water supply return temp. and the setting temp.
Parameter 7.4 the automatic constant temp. water supply time setting (work with
parameter 7.1)

3.System State parameter checking:
On the main interface,press

Prg
enter into parameter setting interface,choose
"Main menu " press button,choose "Unit status",press into the mode setting,press
to view the paramter, press
Ese
return to the previous menu.

Prg

Ese
Main menu Maintenance Clock
Water supply setting

Prg

Ese
Mode select
Unit status

Prg

Ese
Inlet water 12
Outlet water 8
Hot water temp. 25
Ambient temp. 25
Coil temp. 25
Discharge temp. 95
Solar temp. 30
Compressor On

Press button

Unit State parameters
Press button

Display	Status	Means
Inlet water	12	Water inlet temp.
Outlet water	8	Water outlet temp.
Hot water temp.	25	Hot water tank temp.
Ambient temp.	28	Ambient temp.
Coil 1temp.	25	System 1 coil temp.
Coil 2temp.	25	System 2 coil temp.

Display	Status	Means
Discharge 1 temp.	85	System 1 discharge temp.
Discharge 2 temp.	85	System 2 discharge temp.
Solar temp.	30	Solar collector temp.
Return temp.	40	Water supply return temp.
Compressor 1	On	System 1 compressor On/off
Compressor 2	On	System 2 compressor On/off
4way-valve	On	System 4-way valve on/off
H.W.pump	On	Hot water pump On/off
A.C. Pump	On	Air condition water pump on/off
Solar pump	On	Solar water cycle pump on/off
Fan motor	On	Fan motor on/off
3way-valve	On	3-way valve on/off
Aux.electric	On	Auxiliary electric heater on/off
Unload valve	On	System unload valve on/off
EVI valve	On	System EVI valve on/off
Supply output	On	Supply output on/off
H.W.flow sw	Close	Hot water side water flow switch
A.C.flow sw	Close	Air condition side water flow switch
Sys.1 HP sw	Close	System 1 high pressure switch
Sys.1LP sw	Close	System 1 low pressure switch
Sys.2 HP sw	Close	System 2 high pressure switch
Sys.2 LP sw	Close	System 2 low pressure switch
On/off sw	Close	Unit turn on/off switch
Mode sw	Close	Unit mode switch
Electric sw	Open	Turn on/off auxiliary electric mode
A.C.on/off sw	Close	Air condition turn on/off switch
Phase PT sw	Close	Power phase protection
Aux.elec.PT sw	Close	Auxiliary electric protection switch

4. System parameter setting:
On the main interface,press the button

Prg

enter into page2(picture1),press

Prg
for 5 second until hear the beep ,one more parameter parameter)appear, press
to view the parameter, choose Parameter and press to enter the paremters setting interface,press to view the parameter,press to enter the paremters setting interface press to view the parameter, press
to enter the system paremters setting interface,corresponding parameter flashing,
press to modify,press

Ese
to return previous menu.

Prg

Ese
Main menu Maintenance Clock
Water supply setting

Prg

Ese
Main menu Parameter Maintenance Clock
Water supply setting

Press
Prg
button for 5 second until hear the beep
4.1 Detailed description of the function parameters
Parameters 1.0 select Temp.setting
Parameter 1.1:Under hot water mode the setting of water tank temperature.

Prg

Ese
1.1 Hot water temp. 55
1.2 H.W. T 5
1.3 Heating temp. 40
1.4 Heating T 5

1.5 Cooling temp. 12
1.6 Cooling T 5
Parameter 1.2:Under hot water mode,the compressor restart difference temperature. Parameter 1.3:Under heating mode, the setting of water inlet temperature .
Parameter 1.4:Under heating mode, the compressor restart difference temperature. Parameter 1.5:Under Cooling mode, the setting of water inlet temperature .
Parameter 1.6:Under Cooing mode, the compressor restart difference temperature.

Parameters 2.0 select Defrost
Parameter 2.1: Cycle defrost cycle time setting.

Prg

Ese
2.1 Def. cycle
2.2 Def. inlet temp.
2.3 Def. outlet temp.
2.4 Def. max. time
40M
-7
13
8M
Parameter 2.2: Into the defrost state conditions. When the coil temperature is below this parameter setting, the conditions are met.
parameter 2.3: Exit defrost state condition 1, when the coil temperature is higher than the set value of this parameter, the condition is met.
parameter 2.4: out defrost state condition 2, when the defrost time is running
larger than this parameter setting the time, conditions are met.

Parameters 3.0 select Aux-heating
Parameter 3.1:The auxiliary electric heater restart difference temperature.

Prg

Ese
3.1Aux.elec. T
3.2Aux.start delay
3.3 Ambient temp.set
5
30M
15
Parameter 3.2: Auxiliary electric heater start delay time (the time to delay after unit power on, the electric heater allows to output).
Parameter 3.3:The auxiliary electric heater start ambient temperature(When the ambient temperature is below the set temperature, the electric heating
allows the output .

Parameters 4.0 select Systems
Parameter 4.1: Power-down memory options parameters.

Prg
4.1 Power memory
4.2 Economic mode
4.3 H.W.pump
4.4 EVI valve
4.5 Comp.PT temp.
4.6 E.H.H.W.pump
4.7 Cooling mode
On Off Normal
5
105
Special
Off
On: with memory Off: without memory Parameter 4.2:Whether turn on the economic mode. Parameter 4.3: Hot water cycle pump working way.
Normal: when the hot water tank temperature reach the setting temperature the
Ese
4.8 Elec.mode
Heat&H.W
hot water pump stop working.
Special: when the hot water tank temperature reach the setting temperature the hot water pump keep working.

Parameter 4.4:The setting of ambient temperature to turn on the EVI valve.
Parameter 4.5: Compressor discharge temperature too high protection exhaust temperature setting. Parameter4.6 When the unit running manual electric heating mode the hot water cycle pump working way.
Special:the hot water cycle pump required output. Normal:the hot water cycle pump not required output.
Parameter4.7 Whether open the cooling function to the user interface
On:open Off: don t open
Parameter4.8 The application of manual electric heater
Heat: air condition heating auxiliary electric heater
Heat+H.W: air condition heating and hot water auxiliary electric heater
Parameter4.9 System number select
1:single system 2:double system
Parameter4.10 Unit stop temp.(the temp.setting of ambient temp.too low protection)

Parameters 5.0 select Solar setting

Parameter 5.1: Solar pump starts difference temperature set. The difference

Prg

Ese
5.1 Solar start T 6
5.2 Solar stop T
temperature of solar collectors measured values and hot water tank measured temperature.
Parameters 6.0 select Water pump testing

Prg

Ese

H.W. pump A.C. pump Solar pump
3way-valve
Supply output

on/off on/off on/off on/off on/off
Parameter 6.0: This parameter is used by engineers debugging parameters, you can manually open the air-conditioning pumps, water pumps, solar water pump
3way-valve and supply output parameter.

5. The maintenance time inquires

In the interface ,press
Prg
to enter parameter setting interface,choose "Maintenance''
and press to enter Maintenance time inquires, press to turn a choice,
and press
Ese
key returns the last menu.

Prg

Ese

09:50
Main menu		1: E01	2010-01-14	09:00
Parameter		2: P01	2010-01-14	09:10
Maintenance		3: E08	2010-01-14	09:30
Clock Prg / Water supply setting		4: E05	2010-01-14	09:40
		5: P06	2010-01-14
		6: P08	2010-01-14
Ese		7: P12	2010-01-14	10:10
		2010-01-14	10:20

10:00

Picture1		Picture2
NOTE:In the picture 2 interface,press the	prg	button for 5 seconds ,the fault record will

remove.

6. Date/ time/ timing on and off settings
In the main interface, press
Prg
key to enter the parameter setting interface, select
Clock, press key to enter the time setting / timing on or off interface, press the key to turn options:
Note: Press
Prg
button for 5 seconds, when you hear the beep sound, you can see
the page to add Timer on and Timer off select column.

Prg
Date	2010-04-15		Date	2010-04-15
Clock	18:30		Clock	18:30
			Timer on	X
		Prg	Timer off	X

Ese
Ese

Press
Prg
button for 5 second until hear the beep

6.1 . When you select "Date", press key, the date of the year setting flash, press the key to modify Year, then press key again, the month setting flash,press the
key to modify the month, click the key again, Day flash, press the
key to modify the day, then press key to confirm and exit, press the return the layer menu.

Ese
button to

6.2. When you select "Clock", press the key, the time hourly position flash, press the
key to modify hour value, then press key, minutes flash, press the
key to modify the minute value, press the key again confirm and exit, press the to return the layer menu.

Ese
6.3. When you select "Timer on", press the key, regular on or off setting flash, press key to modify the boot time whether on / off, appear " " symbol when choose on,
and show regular boot time settings, click the key, regular on or off hour value setting flash, press the key to modify the value, then press key, regular on or off minute
value setting flash, press key to modify the value, press key to confirm and exit,
press the
Ese
"Ese" to return the layer menu.

7. Lock button/Defrost status/ Fahrenheit and Celsius change:

A: Display Lock Under the main interface :Press

Prg

for 5s, the interface will show the
icon as shown in figure .then, all buttons on the display are locked, but it can be
unlocked after pressing
Prg
for 5s again.
B:Defrost status :When the unit are running heating or hot water mode, if the main interface is showing the icon as shown in figure ,that means the unit are running the defrost status

C: Fahrenheit and Celsius change Under the Celsius status, press

Ese
for 10 s can changed Fahrenheit ,it will cha nge to Celsius again when press for 10s.
Ese
Defrost status icon

Lock icon

Prg

Ese
MODE

A.C. water Inlet Hot water tank Solar Collector Ambient temp.
2011-04-08 11:25
Off

12

25
25
30

Timer icon

8. Fault code display

When a fault, unit controller display automatically corresponding fault code and the fault reasons. When fault resolution, fault display automatically eliminate or after re-power to eliminate.
9. Parameter Table

setting range

2:double system
Display code1	Display code2	Setting data explanation or working state	Parameter	Default	Remarks
Parameter
1.0 Temp.setting	1.1 Hot water temp.	The setting temp.of hot water mode	10 60	55	Adjustable
	1.2 H.W. T	Hot water mode,the compressor / restart difference temperature	1 15	5	Adjustable
	1.3 Heating temp.	The setting temp.of heating mode	15 60	40	Adjustable
	1.4 Heating T	Heating mode,the compressor / restart difference temperature	1 15	5	Adjustable
	1.5 Cooling temp.	The setting temp.of cooling mode	8 28	12	Adjustable
	1.6 Cooling T	Cooling mode,the compressor restart difference temperature	1 15	5	Adjustable
2.0 Defrost	2.1 Def. Cycle	defrosting cycle setting	30min 90min	40min	Adjustable
	2.2 Def. inlet temp.	Start defrosting coil temperature setting	-30 -0	-7	Adjustable
	2.3 Def. outlet temp.	Exit defrost temperature setting	1 30	13	Adjustable
	2.4 Def. Max. Time	Defrost time setting	1min 12min	8min	Adjustable
3.0 Aux-heating	3.1 Aux.elec. T	Auxiliary electric heating mode, the electric restart difference temp.	1 15	5	Adjustable
	3.2 Aux.start delay	Auxiliary electric heater start delay	3min 90min	30min	Adjustable
	3.3 Ambient temp.s et	Auxiliary electric heater start to work when ambient temperature lower than the setting value	-20 45	15	Adjustable
4.0 Systems	4.1 Power memory	Power-down memory options parameters.	ON/OFF	ON	ON: with / OFF: without
	4.2 Economic mode	Whether turn on the economic mode parameters.	ON/OFF	OFF	ON: automatic / OFF: manual
	4.3 H.W.pump	Hot water pump working way	Special/Normal	Special	Special: turn on / Normal: turn off
	4.4 EVI valve	The setting of turn on EVI valve / (effective for the EVI unit)	-20 ~ 30	5	Adjustment
	4.5 Comp.PT temp.	Compressor discharge temp.too high protection setting.	30 ~ 125	105	Adjustment
	4.6 E.H.H.W.pump	Electric heating mode, hot water pump working way.	Special/Normal	Special	Adjustment
	4.7 Cooling mode	Wether open the cooling function to the / interface of user	ON/OFF	Off	Adjustment
	4.8 Elec.mode	The use of manual electric heating mode	Heat/Heat&H.W	Heat&H.W	Adjustment
	4.9 System number	System number select	1:signle system	1	Adjustment
	4.10 Unit stop temp.	The temp.setting of ambient temp. Too low protection	-30 ~ 10	-15	Adjustment
5.0 Solar setting	5.1 Solar start T	Solar start temperature difference / setting	1 ~ 20	6	Adjustment
6.0 Water pump testing	H.W. Pump	Hot water pump testing	ON/OFF	OFF	Adjustment
	A.C. pump	Air conditioner pump testing	ON/OFF	OFF	Adjustment
	Solar pump	Solar pump testing	ON/OFF	OFF	Adjustment
	3way-valve	3way-valve testing	ON/OFF	OFF	Adjustment
	Supply output	Supply output testing	ON/OFF	OFF	Adjustment
7.0 Water supply testing	Water supply	Turn on /turn off the automatic water supply function	On: turn on / Off: turn off	OFF	Adjustment
	Supply temp.	The setting temperature of water supply return temp.	30 ~ 55	40	Adjustment
	Supply T	The water supply pump restart work difference temperature	2 ~ 30	5	Adjustment
	Timer	The automatic water supply function time setting	00:00~ 24:00		Adjustment

IV. Installation sketch
1.Hot water mode installation drawing

Water supply

Hot water

Auxiliary electric

Auxiliary electric

Floor heating
Unit electric box
return temp.
tank temp.
heater power input
heater power
Hot water pump (air condition) pump Water supply
Outdoor fan
Three way valve

CN9
output
power output
power output
pump power
output

power output
power output
R S T N

L N 1 2 L N 1 2

L N 1 2 L N

Power input
(380VAC/3PH/50Hz)
A B

7 3 5
1 8

Wire controller

A Cold water inlet

2 3

6
Cold water inlet
    B

5

8 1 7
4 Power
(220V ~)
L N
1

Legend:

Globe valves
Electric driven two-way valve

Shower head
1 Unit

8 Outdoor fan unit

Check valve

Water pressure switch

2 Water filling valve

3 Water supply return valve
A Water supply return temp.

B Hot water tank temp.

Air-break switch

Water temp. sensor
4 Open wide type hot water tank

5 Water supply cycle pump

Expansion Tank
6 Bath room
7 Hot water cycle pump

The parameter setting for domestic hot water model:

Parameter
1.1 Hot water temp.	The setting temp.of hot water mode	10 60	55	Adjustable
1.2 H.W. T	Hot water mode,the compressor / restart difference temperature	1 15	5	Adjustable
4.3 H.W.pump	Hot water pump working way	Special/Normal	Normal	Special: turn on / Normal: turn off
7.1 Water supply	Turn on /turn off the automatic water supply function	On: turn on / Off: turn off	On	Adjustable
7.2 Supply temp.	The setting temperature of water supply return temp.	30 ~ 55	40	Adjustable
7.3 Supply T	The water supply pump restart work difference temperature	2 ~ 30	5	Adjustable
7.4 Timer	The automatic water supply function time setting	00:00~ 24:00	16:00~ 23:00	Adjustable

NOTE 1 :When the water supply system with water pressure switch , use the water pressure switch control water supply pump independently , as shown in figure, if do not installed water pressure switch ,then connect the water supply pump to water supply output port
2.Heating mode installation drawing

CN9

Auxiliary electric

Auxiliary electric
Unit electric box
heater power input
heater power
Hot water pump
Floor heating
Water supply
Outdoor fan
Three way valve
output
power output (air condition) pump
power output

pump power
output

power output
power output
R S T N

L N 1 2 L N 1 2

L N 1 2 L N

Wire controller

Power input
(380VAC/3PH/50Hz)

22 23

SW6(Air condition turn on/turn off switch)
close circuit :turn on open circuit: turn off
220V/50HZ
LN

23 1 22

L
2 220V/50HZ
5 3 N
6 5 6
4

7 8
thermostat controller

three-way valve
Relay

L
220V/50HZ
N

9 10

11 12

9 10
thermostat controller three-way valve
Relay

L
220V/50HZ
N

13 14

15 16

1 3 1 4
thermostat controller three-way valve
Relay

17
thermostat controller

L
220V/50HZ
N
19

20

21 18
17
three-way valve
Relay
pump power switch

21

Flexible connectors
Globe valves
Electric driven two-way valve

Electric three-way valve

Check valve
    Thermostat

    Expansion Tank

Hot water cycle pump
Unit	12	Room 4 Radiators	21 Swimming pool side water cycle pump
Buffer tank	13	Room 5 electric three-way valve	22	Hot water cycle pump
Water distribution device			23	Outdoor fan unit

1

2

3
4 Water collection device

5 Room 1electric three way valve
6 Room 2 electric three way valve

7 Room 1 floor heating

8 Room 2 floor heating

9 Room 3 electric three way valve
10 Room 4 electric three way valve

11 Room 3 Radiators
14 Room 6 electric three-way valve
15 Room 5 fan coil
16 Room 6 fan coil

17 Swimming pool three-way valve
18 Water to water excharge

19 Swimming pool
20 Sand cylinder filter
3.Hot water&Heating mode Hot water &cooling mode installation drawing

CN9

Water supply

Hot water

Auxiliary electric

Auxiliary electric
Unit electric box
return temp.
tank temp.
heater power input
heater power
output
Hot water pump
power output
Floor heating
(air condition) pump power output

Water supply
pump power output
Outdoor fan
power output
Three way valve
power output
R S T N

L N 1 2 L N 1 2

L N 1 2 L N

Wire controller A B

Power input
(380VAC/3PH/50Hz)

27 25

28 1

1
Note 1 1 24

28 1

B
22
27 23

24 A
26
25

2
power on : port 1 and 2 are connected power up : port 1 and 24 are connected
SW6(Air condition turn on/turn off switch)
close circuit :turn on open circuit: turn off

2
220V/50HZ
LN

L
220V/50HZ
5 3 N
6 5 6
4

7 8
thermostat controller

three-way valve
Relay

L
220V/50HZ
N

9 10

11 12

9 10
thermostat controller three-way valve
Relay

L
220V/50HZ
N

13 14

15 16

1 3 1 4
thermostat controller three-way valve
Relay

17
thermostat controller

L
220V/50HZ
N
19

20

21 18
17
three-way valve

Relay
pump power switch

21

Flexible connectors
Globe valves
Electric driven two-way valve

Electric three-way valve
5 Room 1electric three way valve
6 Room 2 electric three way valve

7 Room 1 floor heating

8 Room 2 floor heating
17 Swimming pool three-way valve
18 Water to water excharge

19 Swimming pool
20 Sand cylinder filter
Check valve
    Thermostat

    Expansion Tank

Hot water cycle pump

1 Unit

2 Buffer tank
9 Room 3 electric three way valve
10 Room 4 electric three way valve

11 Room 3 Radiators
12 Room 4 Radiators

13 Room 5 electric three-way valve
14 Room 6 electric three-way valve

21 Swimming pool side water cycle pump
22 Solar

23 Solar water pump

24 Hot water tank
25 Water supply pump
26 Bath room
3 Water distribution device
4 Water collection device
15 Room 5 fan coil
16 Room 6 fan coil

27 Hot water cycle pump
28 Outdoor fan unit
V. Maintenance and repair
1.Malfunction Indicating Table. Determine and solve the malfuction by malfuction code as below:
1.1.operate display fault code mode

Wire / Controller	Malfunction	Reason	Resolution
E01	Hot water tank temp. Sensor failure	The sensor is open or short circuit	Check or change the sensor
E02	Water inlet temp. Sensor failure	The sensor is open or short circuit	Check or change the sensor
E03	Water outlet temp. Sensor failure	The sensor is open or short circuit	Check or change the sensor
E04	System1 Coil sensor failure	The sensor is open or short circuit	Check or change the sensor
E05	System 2 Coil sensor failure	The sensor is open or short circuit	Check or change the sensor
E06	Outdoor environment temp. Sensor failure	The sensor is open or short circuit	Check or change the sensor
E07	Water supply return temp. Sensor failure	The sensor is open or short circuit	Check or change the sensor
E08	System 1 discharge sensor failure	The sensor is open or short circuit	Check or change the sensor
E09	System 2 discharge sensor failure	The sensor is open or short circuit	Check or change the sensor
E10	Communication failure	Wire controller and The / PCB connection failure.	Check the wire connection
E11	Solar collector temp. Sensor failure	The sensor is open or short circuit	Check or change the sensor
P01	Phase failure protection	Power supply phase failure /lacking	Check whether power supply phase failure or lacking, if failure, please connect it in according to the proper way.
P02	Electric heater auxiliary overheating / & dry heating protection	The overheat protection is opened	Check whether the water flow and electric heating / is working normal then push the reset button on the overheat protection switch.
P03	Hot water flow switch protection	No water/little water in water system.	Check the water flow volume, water pump is failure or not.
P04	Air condition (Floor heating) side water flow switch protection	No water/little water in water system.	Check the water flow volume, water pump is failure or not.
P05	System 1 high pressure protection	System 1 high pressure switch protection	Check whether the pressure switch and system return route failure.
P06	System 1 low pressure protection	System 1 low pressure switch protection	Check whether the pressure switch and system return route failure.
P07	System 2 high pressure protection	System 2 high pressure switch protection	Check whether the pressure switch and system return route failure.
P08	System 2 low pressure protection	System 2 low pressure switch protection	Check whether the pressure switch and system return route failure.
P09	3 times of excessive temp. differentials of inlet water / and outlet water in 30minutes	Water flow volume not enough, water pressure difference is too low	Check the water flow volume, / or water system is blocked or not.
P10	Antifreezing protection in winter	when the outdoor temp. below 0 under standby model	after the antifreezing procedure ,unit will return to the original state automatically
P11	System 1 discharge temp. too high protection	1.whether gas of system leak or not / 2.the tank temp. Be set too high	1 check the refrigerent amount in the system / 2 check whether the tank temp. Setting value too high
P12	System 2 discharge temp. too high protection	1.whether gas of system leak or not / 2.the tank temp. Be set too high	1 check the refrigerent amount in the system / 2 check whether the tank temp. Setting value too high

VI. Wiring diagram
1 2 3 4
1. Mk3092 PCB input and output port definition

CN10

CN9
47	46	45	44	43	42	41	40	39	38	37	36	35	34	33	32	31	30	29	28	27	26	25	24		23	22	21	20	19	18	17	16	15	14	13	12	11	10	09

CN2

RP4
IC7

RP1

CC394B-V1.1
ON DIP
W101122
CN3

Mk3 0 9 2
E-VALVE2

CN1
08
07
06
05
04
03
02
01

E-VALVE1

IC12
IC6

TRAN-IN
FUSE
N3

N2
AC-L

AC-N

RY1

RY2 RY3 RY4 RY5 RY6 RY7 RY8

RY9 RY10 RY11 RY12 RY13
OUT1
OUT2 OUT3 OUT4 OUT5 OUT6 OUT7 OUT8 OUT9 OUT10 OUT11 OUT12 OUT13

NO .	Symbol	Meaning
01	CN1	System 1 coil temp.
02		GND
03		System 1 discharge temp.
04		GND
05		System 2 coil temp.
06		GND
07		System 2 discharge temp.
08		GND
09	CN3	GND
10		Water supply return water temp.
11		GND
12		Outlet water temp.
13		GND
14		Inlet water temp.
15		GND
16		Solar collector temp.
17		GND
18		Ambient temp.
19		GND
20		Hot water tank temp.
21		GND
22		Reservation
23		GND
24	CN2	Turn on/turn off switch 3
25		GND
26		Mode switch 2
27		GND
28		Turn on/off aux.ele heater switch 1
29		GND
30		System 1 high-pressure switch
31		GND
32		System 1 low-pressure switch
33		GND

NOTE 1 : Closed circuit: turn on the manual electric heater mode.
NO .	Symbol	Meaning
34	CN2	Hot water flow switch
35		GND
36		Air condition side water flow switch
37		GND
38		System 2 high-pressure switch
39		GND
40		System 2 low-pressure switch
41		GND
42		Hot water electric heating protection switch
43		GND
44		Turn on/off air heating/cooling switch 4
45		GND
46		Phase sequence protection
47		GND
	OUT1	Compressor of system 1
	OUT2	Compressor of system 2
	OUT3	Fan motor
	OUT4	Unload valve
	OUT5	4 way valve 1
	OUT6	Hot water cycle pump
	OUT7	Floor heating(air condition) water cycle pump
	OUT8	Solar water cycle pump
	OUT9	Hot water auxiliary electric heating
	OUT10	Three-way valve
	OUT11	EVI valve(effective for the EVI unit)
	OUT12	Compressor crankshaft heater
	OUT13	Water supply output
	AC-L	Power Input
	AC-N	Power Input
	N2	Power Input(AC-N)
	N3	Power Input(AC-N)
	TRAN-IN	Transformer input
	CN9	Wire controller
	CN10	Transformer output

Open circuit : turn off the manual electric heater mode
NOTE 2 : Only effective when have not connected to the wire controller
Closed circuit: hot water+cooling mode. Open circuit : hot water + heatling mode
NOTE 3 : Useful when use dual energy for stopping compressor
Closed circuit: turn on
Open circuit : turn off
NOTE 4 :Air condition turn on/off switch
Short circuit: turn on the air condition mode(cooling or heating) Open circuit: turn off the air condition mode(cooling or heating)
2. The electrical box of internal structure
FUSE
2
N
16

2.1 Mode:MACHRWS050W/S(E01)
4

3

Power
Run
L1
L2
CON1
IC6
Mk3077
JK1
N
12V-IN 12V-OUT
ON DIP
1 2 3 4
P5
P6
0057W
1

9

AC-N
OUT1 OUT2 OUT3 OUT4 OUT5 OUT6 OUT7 OUT8 OUT9 OUT10 OUT11 OUT12 OUT13
L1
R
S
T
0057W
11
15

2 5
F U S E
04
03
02
01
CN1
RP1
N2
RY1 RY2 RY3 RY4 RY5 RY6 RY7 RY8 RY9 RY10 RY11 RY12
RY13
E-VALVE1
E-VALVE2
A C - L
N
10
L
14

6
I C 7
IC12
TRAN-IN
N3
L N
L1 L2
2
1
R S T
13

7
RP4
1

ON DIP
06
05
CC394B-V1.1
W101122
1 2 3 4
CN3
CN10
CN9
CN2
08
07
SW1
09
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
8
N

NO .
Sign Meaning

NO .
IC6
Sign Meaning
1 TC
Transfer(220VAC/12VAC)
10 Three-way valve power output
2 MK3092 Controller
Mk3092
3 MK3077 Power phase protection board
11 Outdoor fan power output
12 Water supply pump power output
N
4 KM1
5 KA1
6 KA2
7 KA3
8 KA4
9
Compressor A.C.contactor 13
Hot water pump relay 14
Floor heating(air condition) pump relay 15
Solar water cycle pump relay 16
Water supply pump relay
Power 220VAC (public comment -N)
Solar water cycle pump power output Floor heating pump power output Hot water pump power output
Power input(380VAC/3PH/50Hz)
L
12
2.2 Mode:MACHRW100W/S(E01)
L2
IC6
Mk3077
ON DIP
1 2 3 4

1

FUSE
Power
T
CON1
JK1
N
12V-IN 12V-OUT
P5
P6
0057W
L2 N2

L1 N1
L1
3 4 5 6

F U S E
IC12
TRAN-IN
N3
N2
RY1 RY2 RY3 RY4 RY5 RY6 RY7 RY8 RY9 RY10 RY11 RY12 RY13
AC-N
OUT1 OUT2 OUT3 OUT4 OUT5 OUT6 OUT7 OUT8 OUT9 OUT10 OUT11 OUT12 OUT13
A C - L

I C 7

CN3
CN9
CN10
CN2
SW1
CC394B-V1.1
W101122
RP4
RP1
Mk3092
IC6
09
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
ON DIP
1 2 3 4
2
L1
R
S

7 8
CN1
E-VALVE1
E-VALVE2

9
Run
0057W

10 11

01	02	03	04	05	06	07	08

R S T N
L N 1 2
L N 1 2
L N 1 2 L N

12 13 14 15
16 17 18 19

NO .
Sign
Meaning

NO .
Sign Meaning
1 FP1
Auxiliary electric overheating protector
11 Tc
Transfer(220VAC/12VAC)
2 MK3077 Power phase protection board
12 Power input(380VAC/3PH/50Hz)
3 KA2
4 KA3
5 KA4
6 KA1
7
8 MK3092
9 KM1
10 KM2
Hot water pump relay 13
Floor heating(air condition) pump relay 14
Water supply pump relay 15
Outdoor fan power relay 16
Power 220VAC (public comment -N) 17
Controller 18
Compressor A.C.contactor 19
Auxiliary electric heater A.C.contactor
Auxiliary electric heater power input Auxiliary electric heater power output Hot water pump power outpout
Floor heating pump power output Water supply pump power output Outdoor fan power output
Three-way valve power output
3. Mk3077 PCB Power protection board setting
0057W

L1 L2
R
0057W
S
Power
Run
ON DIP
1 2 3 4

CON1
T JK1 IC6
FUSE
 Mk3 0 7 7

N
P5
P6
12V-IN 12V-OUT
NO .	Symbol	Meaning
1	R	Power input
2	S	Power input
3	T	Power input
4	N	Power input
5	P5	Protection signal output
6	P6	Protection signal output
7	12V-IN	power(12VAC)input
8	12V-OUT	power(12VAC)output

3.1.The setting of current protection value
For example:

Symbol :0

Symbol:1010
Symbol	Current value	Symbol	Current value
0011	8A	1010	20A
1101	9A	0010	21A
0101	10A	1100	28A
1001	11A	0100	29A
0001	12A	1000	30A
1110	18A	0000	31A

ON DIP

ON DIP

1 2 3 4
1 2 3 4

3.2 .Mk3077 PCB Power sequence, current protection board failure indication

Run led display Failure indication

ode Default

1flash 1 off L1 side overcurrent protection

M

MACHRW0

80ZB/PS(01) 12A MAC

The solution of fault
( should re-power on the heat pump after below operation)

Mode Default

1:Check whether the 3-phase poewr miss phase.

HRW150ZB/PS(01) 18A
2:check whether the AC contactor's retral contacting normal or not.
5flash 1 off

MACHRW1

6flash 1 off
L2 side overcurrent protection

Power phase sequence protection

00ZB/PS(01) 18A MAC
1:Check whether the 3-phase poewr miss phase.
2:check whether the AC contactor's retral contacting normal or not.
1:Check whether the 3-phase power sequence is right or wrong .

HRW200ZB/PS(01) 20A
2:Check whether the 3-phase power miss phase.

3.3.Every model's factory default value of current protection .

Mode	Default	Mode	Default
MACHRW050W/S(E01D)	18A	MACHRW100W/S(E01D)	21A
MACHRW080W/S(E01D)	18A

3.4.Wiring diagram for wire controller and PCB

Wire controller
(Mk3093)
01
02
03
04
05

Brown

Blue
Yellow

Controller
(Mk3092) CN9
4.Unit wiring diagram

4.1 Mode:MACHRWS050W/S(E01)
OUT9

Wiring diagram(MK3092-0501)
OUT2
OUT6
OUT8
OUT10

T2 T1
T T

N

09
0 8
0 7
0 6
0 5
0 4
0 3
0 2
0 1
T3
10 CN1
OUT7

Fuse(220V/5A) L
OUT4
11
OUT12
OUT13
T4
12
T5 13
14
15
T6 16
T7 17
18
19
T8 20
21
Mk3092

CN3
OUT11
CN10
T R A N - I N

Red
OUT1

FU SE
R S
T

N

0057W
L1

SW1
SW2

SW3

HP1

LP1
SW4
SW5

SW6
FP1
P3
P4
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36 CN2
37
38
39
40
41
42
43
44
45
46
47

KA3
OUT5

Va2

KA1 KA1 KA2 VA1
OUT3

KM1

White

P3
P4 JK1
L2
12V-IN

12V-OUT
IC6
O N D I P
Mk3077
1 2 3 4

0057W
Power
Run

U V W
White Black Red

Compressor
CON1

KM1

L1 L2 N L N
L N 1 2
L N 1 2
R S T N

Three way valve

balck brown blue

Outdoor fan

Water supply

Solar water

Floor heating

Hot water pump

Power input
signal and power
pump power
pump power (air condition) pump

Legend:
output Va3
power output
output
output
power output
power output
(380VAC/3PH/50Hz)
: A.C.contactor/relay coil
: 4 way valve coil

HP1	LP1

:High pressure switch
:Low pressure switch

P4 : Power phase protection switch
P3
KM1: Compressor A.C.contactor
KA1 : Hot water pump relay
KA2 : Floor heating(air condition) pump relay
KA3 : Solar water pump relay KA4 : Water supply pump relay VA1: Four-way valve
VA2: EVI valve
VA3: Three-way valve
FP1

SW1
SW2
SW3

SW4
SW5
:Hot water auxiliary electric heater overload protection switch(short circuit)
: Unit turn on/turn off switch(short circuit)
: Model select switch(short circuit)
: Turn on/off auxiliary electric heater switch
(open circuit)
: Hot water side water flow switch
: Floor heating (air condition)side water flow switch
(short circuit)
T1 T
T2 T T3 T T4 T T5 T
T6 T
T7 T
T8 T
: System coil temp.
: System discharge temp.
: Water supply return water temp.
: Outlet water temp.
: Inlet water temp.
: Solar collector temp.
: Ambient t emp.
: Hot water tank temp.
SW6 : Floor heating(air heating/cooling) turn on/off switch(short circuit)
4.2 Mode:MACHRW100W/S(E01)

Wiring diagram(MK3092-0101)
OUT11

N Fuse(220V/5A)
OUT10
OUT7
OUT5
L
OUT9
OUT4
OUT3
OUT2
OUT1

CN10 TRAN-IN

Controller
OUT13

CN2
47
46
45
44
43
42
41
40
P3
P4
FP1
SW6

LP2
FU SE
T

N

P3
L2
P4

0057W
L1
R
S

0057W
Power
Run
ON DIP
1 2 3 4
White
P1P2

TC
Red

FP1
OUT8
OUT6
39
38
37
36
OUT12
35
34
HP2
SW5
SW4
JK1
12V-IN
CON1
IC6
P5
P6
Blue
White
Black
Red

KM1
	12V-OUT					29
P1 / P2	M k3 0 7 7					28 / 27 / 26
		U V W		KM1		KA1	VA1 KA2 KA3	KM2	VA2 CH1 KA4			25 / 24
				23
		Compressor					22

				20
				19
				18
				CN3	17

				15

				13
	KM2	KA2	KA3	KA4		KA1					12 / 11

White
Black
Red
White
P5 P6
33
32
31
30
LP1
HP1
SW3
SW2

SW1

21

16

14

CN1 10
09
01
02
03
04
05
06
07
08

T10
T T T T T T
T9
T8
T7
T6
T5

R S T N

L N 1 2

L N 1 2

L N 1 2 L N
T T
T1 T2

Auxiliary electric

Auxiliary electric

Hot water pump

Floor heating

Water supply

Outdoor fan

Three way valve
Power input
heater power input
heater power
power output
(air condition) pump pump power power output
power output
(380VAC/3PH/50Hz)
Legend:
: A.C.contactor/relay coil
output
power output
output

P3
: 4 way valve coil
HP1	LP1
:High pressure switch
:Low pressure switch
P4 : Power phase protection switch
: Compressor crankcase heater coil
KM1: Compressor A.C.contacto
KM2: Auxiliary electric heater A.C.contactorr
KA1 : Outdoor fan relay
KA2 : Hot water pump relay
KA3 : Floor heating(air condition) pump relay
KA4 : Water supply pump relay
CH1: Compressor crankcase heater
VA1: Four-way valve
FP1

SW1
SW2
SW3

SW4
SW5
:Hot water auxiliary electric heater overload protection switch
: Unit turn on/turn off switch(closed circuit)
: Model select switch
: Turn on/off auxiliary electric heater switch
(open circuit)
: Hot water side water flow switch
: Floor heating (air condition)side water flow switch
T1 T
T2 T T5 T T6 T T7 T
T8 T
T9 T
T10 T
: System coil temp.
: System discharge temp.
: Water supply return water temp.
: Outlet water temp.
: Inlet water temp.
: Solar collector temp.(5K resistance)
: Ambient t emp.
: Hot water tank temp.
VA2: EVI solenoid valve
SW6 : Floor heating(air heating/cooling) turn on/off switch(close circuit)

4.3 Outdoor unit(Mode:MAFP050A MAFP080A MAFP100A)

WIRING DIAGRAM (F03)

Orange Red
Orange Red

Capacitor Capacitor

Fan
Fan

Yellow/green

White
Black

L N

Coil sensor Ambient sensor
Power input
(220~240VAC)
CODE:MK3092-01 MK3092/MK3093

M A C O N

AIR TO WATER HEAT PUMP

Tel of Marketing Dept: +86-757-23669556
Tel of sales service Dept: +86-757-23669555
Fax: +86-757-23669554
Postal Code: 528322
Http:// www.macon.com.cn
E-mail:sales@macon.com.cn
Add No.12,Fuan 1 st Industrial Area, Leliu Town, Shunde District, Foshan City
Guangdong Province, China